{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":27,"n_cols":8,"rows_kept":27,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ABQ-C / AZQS-B(8)V1"]
[]
[]
[]
[]
["","","","","ABQ71CV1 / AZQS71B2V1B","ABQ100CV1 / AZQS100B8V1B","ABQ125CV1 / AZQS125B8V1B","ABQ140CV1 / AZQS140B8V1B"]
["Cooling capacity","Nom.","","kW","6.8","9.5","12.1","13.0 (1)"]
["Space cooling","SEER","","","4.65","4.65","","5.01"]
["","Annual energy consumption","","kWh/a","512","716","","1,559"]
["","Capacity","Pdesign","kW","6.80","9.50","","13.0"]
["","Energy efficiency class","","","B","B"]
["Space heating (Average climate)","Capacity","Pdesign","kW","5.65","6.78","","12.3"]
["","SCOP/A","","","3.80","3.80","","3.58"]
["","Energy efficiency class","","","A","A"]
["","Annual energy consumption","","kWh/a","2,082","2,498","","4,811"]
["Nominal efficiency","EER","","","2.91","2.62","2.81","3.36 (3)"]
["","Annual energy consumption","","kWh","1,165","1,813","2,153"]
["","COP","","","3.51","3.42","3.41"]
["","Energy labeling Directive","Cooling","","C","D","C"]
["","","Heating","","B","B","B"]
["Heating capacity","Nom.","","kW","7.5","10.8","13.5","15.5 (2)"]
["Notes","","","","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(3) - EER/COP according to Eurovent 2012, for use outside EU only"]
["","","","","","(4) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(4) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2"]
["","","","","","(5) - See separate drawing for electrical data","(5) - See separate drawing for electrical data"]
["","","","","","(6) - Contains fluorinated greenhouse gases","(6) - Contains fluorinated greenhouse gases"]