{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":13,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWB-BT"]
[]
[]
[]
[]
["","","","","","FWB02BATN6V3","FWB03BATN6V3","FWB04BATN6V3","FWB05BATN6V3","FWB06BATN6V3","FWB07BATN6V3","FWB08BATN6V3","FWB09BATN6V3"]
["Sound pressure level","Fan speed 1","","","dBA","31 (4)","31 (4)","33 (4)","34 (4)","34 (4)","34 (4)","48 (4)","48 (4)"]
["","Fan speed 7","","","dBA","53 (4)","53 (4)","53 (4)","55 (4)","55 (4)","55 (4)","64 (4)","64 (4)"]
["","Fan speed 6","","","dBA","47 (4)","47 (4)","47 (4)","51 (4)","51 (4)","51 (4)","62 (4)","62 (4)"]
["Total sound power level","Fan speed 7","","","dBA","58 (3)","58 (3)","58 (3)","60 (3)","60 (3)","60 (3)","69 (3)","69 (3)"]
["","Fan speed 1","","","dBA","36 (3)","36 (3)","38 (3)","39 (3)","39 (3)","39 (3)","53 (3)","53 (3)"]
["","Fan speed 6","","","dBA","52 (3)","52 (3)","52 (3)","56 (3)","56 (3)","56 (3)","67 (3)","67 (3)"]
["Water flow","Cooling","","Fan speed 1","l/h","219 (1)","256 (1)","283 (1)","318 (1)","400 (1)","465 (1)","683 (1)","758 (1)"]
["","","","Fan speed 7","l/h","418 (1)","502 (1)","555 (1)","799 (1)","847 (1)","1,009 (1)","1,028 (1)","1,162 (1)"]
["","","","Fan speed 6","l/h","369 (1)","471 (1)","519 (1)","715 (1)","744 (1)","894 (1)","1,015 (1)","1,147 (1)"]
["","Heating","","Fan speed 1","l/h","242 (2)","256 (2)","265 (2)","372 (2)","448 (2)","469 (2)","714 (2)","768 (2)"]
["","","","Fan speed 6","l/h","395 (2)","456 (2)","487 (2)","738 (2)","802 (2)","860 (2)","1,028 (2)","1,134 (2)"]
["","","","Fan speed 7","l/h","442 (2)","486 (2)","521 (2)","819 (2)","898 (2)","969 (2)","1,040 (2)","1,148 (2)"]
["","Water pressure drop","Heating","Fan speed 1","kPa","2 (2)","3 (2)","2 (2)","3 (2)","2 (2)","3 (2)","6 (2)","5 (2)"]
["","","","Fan speed 7","kPa","6 (2)","9 (2)","7 (2)","11 (2)","6 (2)","9 (2)","11 (2)","11 (2)"]
["","","","Fan speed 6","kPa","5 (2)","8 (2)","6 (2)","9 (2)","5 (2)","8 (2)","11 (2)","11 (2)"]
["","","Cooling","Fan speed 6","kPa","6 (1)","11 (1)","8 (1)","11 (1)","7 (1)","10 (1)","13 (1)","13 (1)"]
["","","","Fan speed 7","kPa","9 (1)","12 (1)","10 (1)","13 (1)","8 (1)","12 (1)","14 (1)","13 (1)"]
["","","","Fan speed 1","kPa","3 (1)","4 (1)","3 (1)","4 (1)","3 (1)","3 (1)","7 (1)","6 (1)"]
["Piping connections","Drain","","OD","mm","17","17","17","17","17","17","17","17"]
["Power input","Fan speed 6","","","kW","0.085","0.085","0.085","0.167","0.167","0.167","0.252","0.252"]
["","Fan speed 1","","","kW","0.03","0.03","0.03","0.08","0.08","0.08","0.16","0.16"]
["","Fan speed 7","","","kW","0.106","0.106","0.106","0.192","0.192","0.192","0.294","0.294"]
["Dimensions","Unit","","Width","mm","1,040","1,040","1,040","1,390","1,390","1,390","1,740","1,740"]
["","","","Depth","mm","239","239","239","239","239","239","239","239"]
["","","","Height","mm","551","551","551","551","551","551","551","551"]
["Water connections","Primary coil","","","inch","3/4 \"","3/4 \"","3/4 \"","3/4 \"","3/4 \"","3/4 \"","3/4 \"","3/4 \""]
["Weight","Unit","","","kg","26.0","27.0","29.0","35.0","37.0","39.0","47.0","49.0"]
["Fan","Available static pressure","","Fan speed 1","Pa","19","19","19","10","10","16","32","32"]
["","","","Fan speed 7","Pa","72","70","70","79","79","79","80","80"]
["","","","Fan speed 6","Pa","66","60","60","70","70","70","71","71"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Fan speed 7","kW","1.65 (1)","1.90 (1)","2.07 (1)","3.12 (1)","3.33 (1)","3.82 (1)","3.90 (1)","4.39 (1)"]
["","","","Fan speed 6","kW","1.48 (1)","1.81 (1)","1.95 (1)","2.80 (1)","2.95 (1)","3.38 (1)","3.89 (1)","4.37 (1)"]
["","","","Fan speed 1","kW","0.93 (1)","1.01 (1)","1.09 (1)","1.56 (1)","1.73 (1)","1.86 (1)","2.67 (1)","2.92 (1)"]
["","Total capacity 2-pipe","","Fan speed 6","kW","2.07 (1)","2.66 (1)","2.94 (1)","4.00 (1)","4.17 (1)","5.04 (1)","5.67 (1)","6.43 (1)"]
["","","","Fan speed 7","kW","2.32 (1)","2.82 (1)","3.13 (1)","4.47 (1)","4.74 (1)","5.69 (1)","5.70 (1)","6.48 (1)"]
["","","","Fan speed 1","kW","1.33 (1)","1.49 (1)","1.67 (1)","2.17 (1)","2.52 (1)","2.80 (1)","3.83 (1)","4.26 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Fan speed 7","kW","2.54 (2)","2.80 (2)","3.00 (2)","4.70 (2)","5.15 (2)","5.56 (2)","5.95 (2)","6.57 (2)"]
["","","","Fan speed 6","kW","2.27 (2)","2.62 (2)","2.80 (2)","4.24 (2)","4.61 (2)","4.95 (2)","5.91 (2)","6.53 (2)"]
["","","","Fan speed 1","kW","1.39 (2)","1.48 (2)","1.53 (2)","2.14 (2)","2.81 (2)","2.71 (2)","4.11 (2)","4.42 (2)"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741","(3) - Sound power level according to ISO3741"]
["","","","","","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit."]