{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":67,"n_cols":18,"rows_kept":67,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWM-DAT"]
[]
[]
[]
[]
["","","","","","FWM01DATV3","FWM15DATV3","FWM15DATVS","FWM02DATV3","FWM02DATVS","FWM25DATV3","FWM03DATV3","FWM35DATVS","FWM04DATV3","FWM04DATVS","FWM06DATVS","FWM08DATV3","FWM10DATV3"]
["Sound pressure level","Fan speed 1","","","dBA","","","27 (6)","","27 (6)","","","30 (6)","","30 (6)","34 (6)"]
["","Low","","","dBA","32 (6)","33 (6)","","35 (6)","","30 (6)","31 (6)","","30 (6)","","","42 (6)","44 (6)"]
["","Fan speed 6","","","dBA","","","50 (6)","","50 (6)","","","55 (6)","","55 (6)","55 (6)"]
["","High","","","dBA","42 (6)","44 (6)","","45 (6)","","43 (6)","43 (6)","","48 (6)","","","56 (6)","62 (6)"]
["Total sound power level","Low","","","dBA","37 (4)","38 (4)","","40 (4)","","35 (4)","36 (4)","","35 (4)","","","47 (4)","49 (4)"]
["","Fan speed 1","","","dBA","","","32 (4)","","32 (4)","","","35 (4)","","35 (4)","39 (4)"]
["","Fan speed 6","","","dBA","","","55 (4)","","55 (4)","","","60 (4)","","60 (4)","60 (4)"]
["","High","","","dBA","47 (4)","49 (4)","","50 (4)","","48 (4)","48 (4)","","53 (4)","","","61 (4)","67 (4)"]
["Water flow","Cooling","","Low","l/h","179 (1)","216 (1)","","234 (1)","","275 (1)","302 (1)","","431 (1)","","","682 (1)","706 (1)"]
["","","","Fan speed 1","l/h","","","206 (1)","","221 (1)","","","340 (1)","","431 (1)","457 (1)"]
["","","","Fan speed 6","l/h","","","364 (1)","","449 (1)","","","755 (1)","","902 (1)","915 (1)"]
["","","","High","l/h","264 (1)","299 (1)","","337 (1)","","415 (1)","503 (1)","","743 (1)","","","1,152 (1)","1,376 (1)"]
["","Heating","","Fan speed 1","l/h","","","236 (2)","","246 (2)","","","415 (2)","","430 (2)","526 (2)"]
["","","","Fan speed 6","l/h","","","418 (2)","","445 (2)","","","907 (2)","","1,003 (2)","1,061 (2)"]
["","","","High","l/h","317 (2)","320 (2)","","373 (2)","","469 (2)","506 (2)","","736 (2)","","","1,129 (2)","1,455 (2)"]
["","","","Low","l/h","211 (2)","252 (2)","","260 (2)","","302 (2)","301 (2)","","430 (2)","","","690 (2)","764 (2)"]
["","Water pressure drop","Heating","Fan speed 1","kPa","","","8 (2)","","6 (2)","","","5 (2)","","4 (2)","6 (2)"]
["","","","High","kPa","15 (2)","14 (2)","","12 (2)","","17 (2)","11 (2)","","10 (2)","","","10 (2)","18 (2)"]
["","","","Fan speed 6","kPa","","","21 (2)","","16 (2)","","","21 (2)","","17 (2)","19 (2)"]
["","","","Low","kPa","8 (2)","9 (2)","","6 (2)","","8 (2)","5 (2)","","4 (2)","","","4 (2)","6 (2)"]
["","","Cooling","Fan speed 6","kPa","","","20 (1)","","20 (1)","","","18 (1)","","18 (1)","17 (1)"]
["","","","High","kPa","13 (1)","14 (1)","","13 (1)","","16 (1)","13 (1)","","12 (1)","","","12 (1)","20 (1)"]
["","","","Fan speed 1","kPa","","","8 (1)","","6 (1)","","","4 (1)","","5 (1)","5 (1)"]
["","","","Low","kPa","7 (1)","8 (1)","","7 (1)","","8 (1)","6 (1)","","5 (1)","","","5 (1)","6 (1)"]
["Piping connections","Drain","","OD","mm","16","16","16","16","16","16","16","16","16","16","16","16","16"]
["Power input","Fan speed 6","","","kW","","","0.066","","0.066","","","0.105","","0.105","0.105"]
["","Fan speed 1","","","kW","","","0.02","","0.02","","","0.04","","0.04","0.04"]
["","High","","","kW","0.037","0.053","","0.053","","0.057","0.056","","0.098","","","0.182","0.244"]
["","Low","","","kW","0.02","0.03","","0.02","","0.03","0.03","","0.04","","","0.09","0.11"]
["Dimensions","Unit","","Width","mm","584","584","584","584","584","794","794","1,000","1,000","1,000","1,000","1,210","1,210"]
["","","","Depth","mm","224","224","224","224","224","224","224","224","224","224","224","249","249"]
["","","","Height","mm","535","535","535","535","535","535","535","535","535","535","535","535","535"]
["Water connections","Additional coil","","","inch","","","","","","","1/2\""]
["","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","3/4 \"","3/4 \""]
["Weight","Unit","","","kg","16.5","16.5","16.5","16.9","16.9","21.4","22.1","26.3","26.4","26.4","26.6","35.4","35.4"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Fan speed 6","kW","","","1.51 (1)","","1.83 (1)","","","3.53 (1)","","4.10 (1)","4.10 (1)"]
["","","","Low","kW","0.77 (1)","0.93 (1)","","0.98 (1)","","1.15 (1)","1.23 (1)","","1.76 (1)","","","2.75 (1)","2.94 (1)"]
["","","","Fan speed 1","kW","","","0.88 (1)","","0.92 (1)","","","1.41 (1)","","1.76 (1)","1.92 (1)"]
["","","","High","kW","1.16 (1)","1.25 (1)","","1.37 (1)","","1.82 (1)","2.05 (1)","","3.05 (1)","","","4.73 (1)","5.72 (1)"]
["","Total capacity 2-pipe","","Fan speed 6","kW","","","2.05 (1)","","2.55 (1)","","","4.30 (1)","","5.16 (1)","5.23 (1)"]
["","","","Low","kW","1.02 (1)","1.24 (1)","","1.34 (1)","","1.57 (1)","1.73 (1)","","2.47 (1)","","","3.88 (1)","4.00 (1)"]
["","","","High","kW","1.50 (1)","1.69 (1)","","1.91 (1)","","2.36 (1)","2.87 (1)","","4.23 (1)","","","6.53 (1)","7.78 (1)"]
["","","","Fan speed 1","kW","","","1.18 (1)","","1.27 (1)","","","1.94 (1)","","2.47 (1)","2.63 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","1.82 (2)","1.84 (2)","","2.15 (2)","","2.70 (2)","2.94 (2)","","4.24 (2)","","","6.49 (2)","8.37 (2)"]
["","","","Fan speed 6","kW","","","2.40 (2)","","2.56 (2)","","","5.22 (2)","","5.77 (2)","6.10 (2)"]
["","","","Low","kW","1.21 (2)","1.45 (2)","","1.50 (2)","","1.74 (2)","1.76 (2)","","2.47 (2)","","","3.97 (2)","4.39 (2)"]
["","","","Fan speed 1","kW","","","1.36 (2)","","1.41 (2)","","","2.39 (2)","","2.47 (2)","3.03 (2)"]
["Current input","High","","","A","0.16","0.20","","0.20","","0.27","0.27","","0.40","","","0.80","1.07"]
["","Fan speed 6","","","A","","","0.29","","0.29","","","0.47","","0.47","0.47"]
["","Low","","","A","0.09","0.11","","0.11","","0.14","0.14","","0.19","","","0.39","0.54"]
["","Fan speed 1","","","A","","","0.08","","0.08","","","0.19","","0.19","0.19"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting"]
["","","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit."]